Chopper Interlock Module

Test Plan Document

Implementation in LabVIEW FPGA

| Revision: | 1.0 |
| --- | --- |
| Status: | Draft |
| Repository: | N/A |
| Project: | UPM-GMV-LIPAc Support |
| Last modification: | 3/11/2017 |
| Created: | 18/10/2017 |
| Release Date: | 03/11/2017 |

| Prepared by | Reviewed by | Approved by |
| --- | --- | --- |
| Miguel Astrain | Eduardo Barrera | Mariano Ruiz |

Table of contents

SCOPE	3

TEST PROCEDURES	3

[CIM-GNRL-0000] LabVIEW version control	3

[CIM-GNRL-0001] EPICS CA PV access	3

[CIM-FUNC-0000] CIM enable state test	4

[CIM-FUNC-0001] CIM Duty Cycle monitoring	4

[CIM-FUNC-0002] CIM GATE OFF state check	4

[CIM-FUNC-0003] CIM GATE Rising state check	5

[CIM-FUNC-0004] CIM GATE ON state check	5

[CIM-FUNC-0005] CIM GATE Falling state check	6

[CIM-FUNC-0006] CIM INHIBITION	6

# SCOPE

This document defines the Test Plan for the Chopper Interlock Module. This module contains the FPGA configuration VI and its Project containing an EPICS IOC server and client. The audience of this document are the test engineers who will execute the Test Plan and produce the Test Report.

The test plan covers the following aspects:

- Test procedures for ensuring all requirements are verified.

- Performance tests.

- The tests are classified for the execution of the SAT and FAT.

# TEST PROCEDURES

## [CIM-GNRL-0000] LabVIEW version control

| ##### CIM-GNRL-0000 | LabVIEW version control |
| --- | --- |
| Requirement(s) |  |
| Description |  |
| Pre-requisite |  |
| Procedure |  |
| - Run NI MAX application. - [Checkpoint] Check NI MAX contains - LabVIEW 2014 SP1 f10 - LabVIEW-RT 2014 - LabVIEW DSC 2014 - LabVIEW FPGA 2014 - LabVIEW Xilinx vivado tools 13 - NI-RIO 14.0.1 |  |
| Pass Criteria |  |
| - Software defined in Procedure steps contains the expected versions. |  |

## [CIM-GNRL-0001] EPICS CA PV access

| ##### CIM-GNRL-0001 | EPICS CA PV access |
| --- | --- |
| Requirement(s) |  |
| Description |  |
| Pre-requisite |  |
| Procedure |  |
| Pass Criteria |  |

## [CIM-FUNC-0000] CIM enable state test

| ##### CIM-FUNC-0000 | CIM enable state test |
| --- | --- |
| Requirement(s) |  |
| Description |  |
| - To check CIM maintains FBI =1 when CHOPPER_ON=”1” and FARADAY_IN=”0”. - Change the rest of the signals to check CIM does not trigger and interlock action |  |
| Pre-requisite |  |
| Procedure |  |
| Pass Criteria |  |
| - FBI=1 during the test. |  |

## [CIM-FUNC-0001] CIM Duty Cycle monitoring

| ##### CIM-FUNC-0001 | CIM Duty Cycle monitoring |
| --- | --- |
| Requirement(s) |  |
| Description |  |
| To check correct duty cycle readings. |  |
| Pre-requisite |  |
| Procedure |  |
| With CIM on any post configuration state enable the CHOPPER_ON=”1”. Read the VI front panel readings on duty cycle and change it accordingly. |  |
| Pass Criteria |  |
| - Duty cycle readings agree with the generated values. - Two profiles are supported (3ms, 5%) and (6ms, 10%) - FBI is triggered when defined. |  |

## [CIM-FUNC-0002] CIM GATE OFF state check

| ##### CIM-FUNC-0002 |  |
| --- | --- |
| Requirement(s) |  |
| Description |  |
| CIM monitors the following signals in this state: - SOURCE_GATE: Duty cycle <SRCDuty; Pulse <SRCPulse. - ACCT: Voltage <ACCTThr - VMON: Voltage <VMONThr - CHOPPER_ON - FARADAY_IN - CHOPPER_GATE CIM waits in this state until a rising edge is detected on the CHOPPER_GATE signal. |  |
| Pre-requisite |  |
| Procedure |  |
| - Change ACCT, VMON, CHOPPER_ON, FARADAY_IN signal to go beyond the threshold |  |
| Pass Criteria |  |
| - FBI is triggered when out of operation conditions |  |

## [CIM-FUNC-0003] CIM GATE Rising state check

| ##### CIM-FUNC-0003 |  |
| --- | --- |
| Requirement(s) |  |
| Description |  |
| CIM stays for (GATETRise) on this state. CIM monitors the following signals in this state: - SOURCE_GATE: Duty cycle <SRCDuty; Pulse <SRCPulse. - CHOPPER_GATE - VMON: Voltage - CHOPPER_ON - FARADAY_IN CIM monitors VMON voltage until GATETRise time has passed, if VMON is below (in absolute value) the VMONOff value it shall transition to the next state. |  |
| Pre-requisite |  |
| Procedure |  |
| - Change VMON signal to rise slower until FBI is triggered. |  |
| Pass Criteria |  |
| - FBI triggerend when timing is off resolution. |  |

## [CIM-FUNC-0004] CIM GATE ON state check

| ##### CIM-FUNC-0004 |  |
| --- | --- |
| Requirement(s) |  |
| Description |  |
| CIM monitors the following signals in this state: - SOURCE_GATE: Duty cycle <SRCDuty; Pulse <SRCPulse. - CHOPPER_GATE - VMON: Voltage - CHOPPER_ON - FARADAY_IN In this state CIM monitors VMON is below (in absolute value) the VMONOff value and waits for a falling edge on CHOPPER_GATE when it transitions onto the next state. |  |
| Pre-requisite |  |
| Procedure |  |
| - Short VMON signal duration so that it falls before CHOPPER_GATE is “0”. |  |
| Pass Criteria |  |
| - FBI =”0”. |  |

## [CIM-FUNC-0005] CIM GATE Falling state check

| ##### CIM-FUNC-0005 |  |
| --- | --- |
| Requirement(s) |  |
| Description |  |
| CIM stays for (GATETFall) on this state. CIM monitors the following signals in this state: - SOURCE_GATE: Duty Cycle <SRCDuty; Pulse <SRCPulse. - CHOPPER_GATE - VMON: Voltage - CHOPPER_ON - FARADAY_IN CIM monitors VMON voltage until GATETFall time has passed, if VMON is over (in absolute value) the VMONThr value it shall transition back to GATE_OFF. |  |
| Pre-requisite |  |
| Procedure |  |
| - Change VMON signal to fall slower until FBI is triggered |  |
| Pass Criteria |  |
| - FBI triggerend when timing is off resolution. |  |

## [CIM-FUNC-0006] CIM INHIBITION

| ##### CIM-FUNC-0006 |  |
| --- | --- |
| Requirement(s) |  |
| Description |  |
| CIM shall transition into an PRE-ARM |  |
| Pre-requisite |  |
| Procedure |  |
| - Using the LabVIEW EPICS CA Client, write INHIBIT=”1”. |  |
| Pass Criteria |  |
| - CIM correctly transitions into a “disabled/INHIBITED” state, the PRE-ARM state without triggering FBI. |  |